## Inputs
Preliminary design of a 50,000 PE activated sludge works: design basis
Inputs
Parameter | Symbol | Value | Unit | Status and source
Population served | P | 50000 | persons | Design choice (PE=P)
BOD5 per PE | - | 60 | g/d | Definition: Directive 91/271/EEC Art 2(6)
Domestic flow | G | 150 | L/head/d | Guidance: SEPA, typically 150
Infiltration | I | 50 | L/head/d | Assumption
Suspended solids per head | - | 75 | g/head/d | Secondary source: Peiris (WEDC), citing WTI 1994
Ammonia-N per head | - | 8 | g N/head/d | Secondary source: same
Organic N per head | - | 5 | g N/head/d | Weak source: lecture notes, typical 5.4-5.5
COD:BOD ratio | - | 2 | - | Xylem: 1.8-2.2 typical
FFT multiplier | - | 3 | - | SEPA: FFT = 3PG + Imax + 3E
Trade effluent | E | 0 | m³/d | Assumption: domestic only
Winter temperature | Tw | 10 | °C | Assumption, not sourced
Summer temperature | Ts | 20 | °C | Assumption: not sourced
Discharge consents
BOD5 consent | - | 25 | mg/L | Directive Annex I Table 1
COD consent | - | 125 | mg/L | Directive Annex I Table of
SS consent | - | 35 | mg/L | Directive Annex I Table 1 (over 10,000 p.e.)
Ammonia-N consent | - | 5 | mg/L | Assumption (site-specific in reality)
Calculated values
Flow per head, total |  | 200 | L/head/d
Dry weather flow (DWF) |  | 10000 | m³/d
DWF |  | 416.6667 | m³/h
DWF |  | 0.11574 | m³/s
Flow to full treatment (FFT) |  | 25000 | m³/d
FFT |  | 1041.6667 | m³/h
FFT |  | 0.28935 | m³/s
BOD load |  | 3000 | kg/d
BOD concentration |  | 300 | mg/L
SS load |  | 3750 | kg/d
SS concentration |  | 375 | mg/L
Ammonia-N load |  | 400 | kg N/d
TKN load |  | 650 | kg N/d
TKN concentration |  | 65 | mg/L
Ammonia-N concentration |  | 40 | mg/L
COD concentration |  | 600 | mg/L
COD load |  | 6000 | kg/d
Required BOD removal |  | 91.67% | %
Required COD removal |  | 79.17% | %
Required SS removal |  | 90.67% | %
Ammonia removal (vs influent ammonia) |  | 87.5% | %
Check: flow × conc − load |  | 0 | kg/d

## Notes
Design basis is textbook and guidance-based, not measured site data.
Infiltration, trade effluent, temperatures and the ammonia consent are assumptions.
SS and ammonia loads come from a secondary source (WTI 1994 via Peiris, WEDC); organic N comes from lecture notes.
Consent limits are treated as upper limits, which is conservative, since the Directive allows a set number of failed samples.
The Directive’s BOD limit is measured without nitrification, so nitrification oxygen demand is additional.
Item | Value | Unit | Status | Source
Primary overflow rate at DWF | 40 | m³/m²/d | Typical (range 30–50) | SNU lecture notes L14 (ocw.snu.ac.kr)
Primary overflow rate at FFT | 100 | m³/m²/d | Typical (range 80–120) | SNU lecture notes L14
Primary retention time at DWF | 2 | h | Typical (range 1.5–2.5) | SNU L14; CED Engineering text gives 1.5 h before activated sludge
BOD removal | 30 | % | Within 25–40% | SNU L14; CED Engineering primary treatment text
SS removal | 60 | % | Within 50–65% | CED Engineering (SNU L14 gives 50–70%)
COD removal | 30 | % | Assumption (same as BOD) | –
TKN removal | 10 | % | Assumption | –
Ammonia-N removal | 0 | % | Assumption (soluble, unchanged) | –
Number of primary tanks | 2 | – | Design choice | –
Screen velocity through openings | 0.9 | m/s | Within 0.6–1.2 | NPTEL Lecture 21 (screening)
Screen clear spacing | 20 | mm | Design choice (medium screens 20–50 mm) | NPTEL Lecture 21
Screen bar width | 10 | mm | Typical (~10 mm bars) | NPTEL Lecture 21
Clean-screen headloss | 0.0729(V² − v²) | m | Formula from source | NPTEL Lecture 21
Grit detention time at FFT | 180 | s | Assumption | waterandwastewater.com: “30 seconds to several minutes” (page cites no source)
Step 2 criteria come mainly from US and Indian lecture and textbook material, not UK standards.